## interopreability IO list
version revision ref. SSEG Plant DNP3_SCADA_INTERFACE_2022_11_01.xlsx
TELECONTROL PROTOCOL MAPPING FOR A DNP3 LAN SERVER INTERFACE BETWEEN A SCADA CLIENT AND AN EMBEDDED GENERATION PV INSTALLATION( SSEG CATEGORY A3 - >100kVA to <1MVA-Renewable PV Power Plant )
COMMUNICATION DRECTION | SELECTABLE RANGE(UNIT) | SCADA Master TAG DESCRIPTION | PROTOCOL SPECIFIC TELEGRAM TYPE TO CONFIGURE
|  |  | DNP3 ADDRESS | OUTPUT |  | CONTROL direction
|  |  |  | TYPE | object |  |  | variation
Set point from Client | % 0 - 100% ( integer value -for example, 25) | Production Constraint of Generated AC Power (100% production is max declared generation capacity) | 0 | 16 bit Analog control | 41 |  |  | 2
Set point from Client | 5%,10%,15%/minute ( range 0-100)%/Minute | Power Gradient Constraint (Ramp up rate) | 1 | 16 bit Analog control | 41 |  |  | 2
Set point from Client | 5%,10%,15%/minute ( range 0-100)%/Minute | Power Gradient Constraint (Ramp down rate) | 2 | 16 bit Analog control | 41 |  |  | 2
Control functions are configured for select before operate
|  |  | DNP3 ADDRESS | INPUT | EVENT CLASS General interrogation | STATIC |  | EVENT CHANG
|  |  |  | TYPE |  | object | variation | EVENT CLASS | object | variation
Feedback from Server | Watts | Total Power Generated by *EG Plant (AC) | 0 | 32 bit Analog input | 0 | 30 | 5 | 2 | 32 | 7
Feedback from Server | Var | Reactive Power Measurement @ *POC | 1 | 32 bit Analog input | 0 | 30 | 5 | 2 | 32 | 7
Feedback from Server | +Watts Exported/ Watts Imported | Exported Power/ Imported Power - measurement @ *POC | 2 | 32 bit Analog input | 0 | 30 | 5 | 2 | 32 | 7
Feedback from Server | % 0 - 100% ( integer representing the % set point -last update) | Production Constraint of Generated Power(confirmation of last received % set point value echo) | 3 | 16 bit Analog input change with time | 0 | 30 | 4 | 2 | 32 | 4
Feedback from Server | 5%,10%,15%/minute typical ( range 0-100)%/Minute | Power Gradient Constraint UP(confirmation of last received Ramp Up % set point value echo) | 4 | 16 bit Analog input change with time | 0 | 30 | 4 | 2 | 32 | 4
Feedback from Server | 5%,10%,15%/minute typical ( range 0-100)%/Minute | Power Gradient Constraint DOWN(confirmation of last received Ramp Down % set point value echo) | 5 | 16 bit Analog input change with time | 0 | 30 | 4 | 2 | 32 | 4
Feedback from Server | ON/OFF ( alarm condition = ON/true -function disabled) | Production Constraint Mode Function selection (ON/OFF) | 0 | binary input status/change with tme | 0 | 1 | 2 | 1 | 2 | 2
Feedback from Server | ON/OFF ( alarm condition = ON/true - function disabled) | Power Gradient Constraint Mode Function selection (ON/OFF) | 1 | binary input status/change with tme | 0 | 1 | 2 | 1 | 2 | 2
client/ server addressing for compliance testing | DNP3 Client address: 100 | DNP3 Server address: 101 ( for compliance test purposes only-final address will be provided in due course) |  | IPV4 Address of server: to be provided by installer for compliance test purposes only. Final TCPIP configuration parameters will be provided in due course |  |  |  |  | Port #: 20000
The City of Cape Town Municipality will provide the final source and destination addressing of the DNP3 server/client as well as the VPN configuration settings for each SSEG sites TCPIP connection to the SCADA Master Station in due course.
*NOTES | EG = EMBEDDED GENERATION and POC = POINT OF CONNECTION to the CCT electricity supply network
DNP 3 Object and Variation definition list used for interoperability with the City of Cape Town SSEG SCADA interface ( SEL3530-4 Real Time Automation Controller)
Monitoring Direction ( Server to Client) |  |  |  | Control Direction (Client to Server)
Object | Variation | Definition |  | Object | Variation | Definition
30 | 4 | 16 bit Analog Input Without flag |  | 41 | 2 | 16 bit Analogue Output Block
| 5 | 32 bit Analog Input short floating point
32 | 4 | 16 bit Analog Input Event With quality flag and Time stamped
| 7 | 32 bit Analog Input short floating Event With quality flag and Time stamped |  | Note: Time stamping shall be in local time - South Africa Standard Time (UTC +2)
The Client interface will be configured to pole for Class data and disable unsolicited messages from the
1 | 2 | Binary Input With status(Static) |  | DNP3 server
2 | 2 | Binary Input Event change with Time( Event Change)

## compliance tes procedure
SCADA Compliance Test Procedure for Category A3 SSEG Sites
The installer/plant owner must acquire, install and configure a DNP3 server interface prior to requesting a SSEG SCADA compliance test, to be conducted on site. There shall also be a Router
capable to be configured for an IPSec VPN connection to the CCT DNP3 Client interfaced, installed on site.
Compliance tests will be conducted using a SEL3530 Real Time Automation Controller as DNP3 Client simulation interface. The DNP3 Client simulation equipment will be connected directly to a
Cu Ethernet port, located on the DNP3 Server interface or located on an Ethernet switch/router port that is in the same IP network range as the DNP3 Server interface , for the duration of
the compliance test. The DNP3 Server interface must be configured as per the DNP3 protocol mapping list, stated in this document, including all the functional Inputs and outputs as listed.
After the communication between the DNP3 Client simulator (test equipment) and the Installed DNP3 server interface is established the test procedure, as stated below, will start.
The Client interface provides the CCT representative with a web browser based interface to monitor real time performance of all configured inputs and to be able to send set point commands to SSEG's DNP3 server interface complies
the DNP3 server interface in order to verify whether the connected Interface reacts correctly to the CCT SCADA set point command requirements for Category A3 SSEG plants.
The following terminology will be used for ease of reference in the test procedure:
DNP3 Client interface - The CoCT's simulation test equipment is a Remote Terminal Unit (SEL3530 -RTAC) and used to simulate the DNP3 controller to which the DNP3 communication Server interface, installed
at each Category A3 SSEG site, will communicate with once the inter communication is finalized.
DNP3 Server interface - The DNP3 Server interface, installed at each Category A3 SSEG site connects the SSEG inverter controller and translates the Modbus communcation protocol functionality to DNP3
communcation protocol functionality in order to communicate with the CCT DNP3 Client interface.
For ease of explaining the test procedure the following values will be used:
The maximum rated AC generation capacity of this plant is 200 KVA. A Production Constraint set point of 50 % = 100KVA and a Production Constraint set point of 30 % = 60KVA
Please note that weather conditions are taken into consideration when appointments are made for SSEG compliance test i.e. cloud cover, light intensity and so forth. When these conditions change on the day that the tests are conducted then the test procedure will also be adapted accordingly.
Test procedure to verify SSEG SCADA compliance .
1. At the start of the tests the DNP3 Protocol validity attribute of all the configured inputs will be confirmed and must report as valid. (Any Input that reports as Invalid will mean that the input was not correctly configured)
2. Total Power Generated, Reactive Power and Exported/Imported Power analogue values will be verified for accuracy and frequency that updates are received at the Client interface, in real time. These values performance will be monitored throughout the duration of the compliance tests.
3. A 100% Production Constraint set point command will be sent from the DNP3 Client simulator to the DNP3 Server interface to increase the energy production to as much as the SSEG plant can produce at that time.
The Total Power Generated analogue value will be monitored as this value reported from the DNP3 Server Interface to the DNP3 Client simulator reaches its maximum value at which point the value stabilizes and
stops increasing. This value will determine what set points will be applied during the test procedure.
4. The Exported/Imported Power analogue feedback value that is reported to the DNP3 Client Interface will be verified and cross referenced with the instantaneous value recorded by the installed bidirectional energy.
meter's reading. If the load consumes less than the generated kVA then the reported value will have a (+) sign and will be interpreted as surplus energy being exported into the Grid. If the SSEG's total generated
energy is less than the total energy consumed by the load then the Imported /Exported energy analogue feedback value must report a (-) sign which will be interpreted as imported energy form the Grid i.e. the required by the load at the time.
SSEG plant's generating less energy than what is required by the load.
5. The Production Constraint set point will be set to 50% and the SSEG plant's re-action to this new set point will be verified. The Production Constraint set point feedback value must change to 50% and report this
this change in less that 30 seconds after the DNP3 server recieved the command. this Analogue feedback value will be verified for accuraty rate of change and time accuracy of the assositaed time stamp after the
set point was changed. The Total Power Generated analogue value will be monitored and should frequently report a decreasing value till the SSEG plant reaches production constraint set point of 50% and restricts production to this set value. As an example: If the maximum combined AC generation capacity of the
Invertor/s are rated at 200KVA then 50 % will be 100KVA and this value shall be where the SSEG plant will hold the production when the Production Constraint set point was set to 50%
6. The production constraint set point will be set to 30% and the SSEG plant's re-action to this new set point will be verified. The Production Constraint set point feedback value must change to 30% and report this value in less than 30 seconds after the set point command was sent with the accurate time stamp
when the set point was changed. The Total Power Generated analogue value will be monitored and should frequently report a decreasing value till the SSEG plant reaches production constraint set point of 30% and restricts production to this set value. As an example: If the maximum combined AC generation capacity of the
Invertor/s are rated at 200KVA then 30 % will be 60KVA and this value shall be where the SSEG plant will hold the production when the Production Constraint set point was set to 30% .
7. The Power Gradient Constraint Up/Down set point commands will be sent from the Client interface to set the ramp rates to 10%/min for both commands respectively. The response of the associated feedback ( echo)will also be verified to confirm if the correct values of the 10 %/min set points are received from the
DNP3 server and reported to the Client interface, in real time.
8. A Production constraint set point command will be sent from the Client interface to change the SSEG's Production from 30% to 50% and the respective feedback will be verified. The time that it takes to adjust the production constraint by 20% will be monitored to verify if the SSEG Plant reacts correctly by ramping UP
by 10%/min from 50% to 30% production constraint. This test is to verify that the power gradient constraint reacts correctly to the changed production constraint set point, in real time and at the rate at which the Power Gradient UP set point was set to the correct rate of change.
If the SSEG's controller was configured correctly it should take 2 minutes to ramp production up from 30% to 50% at 10%/minute
9. A Production constraint set point command will be sent from the Client interface to change the SSEG's Production from 50% to 30% and the respective feedback will be verified. The time that it takes to adjust the production constraint by 20% will be monitored to verify if the SSEG Plant reacts correctly by ramping
down by 10%/min from 50% to 30% production constraint. This test is to verify that the power gradient constraint re-acts correctly to the changed production constraint set point in real time and at the rate at which the Power Gradient DOWN set point was set to the correct rate of change.
If the SSEG controller was configured correctly it should take 2 minutes to ramp production down from 50% to 30% at 10%/minute
10. All set point values will be restored to the values that were set when the test started. If the DNP 3 server interface and the SSEG plant re-acted to all the set point commands and reported all configured inputs as stated above then the SSEG plant will be considered as compliant and a test reported will be submitted to the
City of Cape Town's Official that is responsible for managing the SSEG application process.